Fire safety log book

# Premises address:
# Log to be kept in this location:

# Introduction to your log book

This fire safety log book has been prepared to assist the ‘responsible person’ in co-ordinating and maintaining a fire safety record keeping system.

This log book gives examples of the main requirements for demonstrating compliance with current fire safety legislation. Your premises may have additional requirements that aren’t covered in this example log book such as sprinkler systems or complex alarm systems. In these situations, you should add additional pages or modify the log book to ensure it is as accurate as possible for your premises.

Fire safety law

There is no statutory requirement to maintain a fire safety log book, but Article 17 of the Regulatory Reform (Fire Safety) Order 2005 requires the ‘responsible person’ for premises to ensure that all fire safety facilities, equipment and devices are maintained in efficient working order and in good repair.

Additionally, Article 21 states that where there are employees, they should be provided with adequate safety training.

The Order also requires that tests, maintenance and safety training are capable of being audited to ensure they are being carried out.

The most effective way of demonstrating compliance with these particular Articles is to keep records, and a log book is one way of doing it.

### Using this log book

The log book should be kept up to date* and readily available for inspection by the Fire and Rescue Service when required.

It is best practice to keep it with any records relating to your current Fire Safety Risk Assessment**

We strongly recommended that where necessary, maintenance contracts are taken out with competent persons (e.g. those registered with NICEIC or ECA for electrical maintenance or registered with BAFE for firefighting equipment).

We recommend that this log book is kept in a loose leaf format, with new record keeping pages being printed, photocopied or downloaded when required.

More information

Information on fire safety law and how to carry out a fire risk assessment can be found on the Devon and Somerset Fire and Rescue Service website: https://dsfire.gov.uk/safety?businesses

# Useful telephone numbers
## In an emergency always dial 999
## Firefighting equipment maintenance and repairs
### Telephone number:

## Emergency lighting maintenance and repairs
### Telephone number:
## Building maintenance
### Telephone number:
## Local Authority Environmental Health Department
### Telephone number:
## Fire alarm maintenance and repairs
### Telephone number:
## Local Fire and Rescue Authority
### Telephone number:

## Health and Safety Executive
### Telephone number:

## Primary Authority Scheme lead
### Telephone number:

## Local Authority Building Control
### Telephone number:

# List of competent persons/fire wardens

Name:
Deputy:
Department:
Telephone number:

Name:
Deputy:
Department:
Telephone number:
Name:
Deputy:
Department:
Telephone number:

Name:
Deputy:
Department:
Telephone number:

Name:
Deputy:
Department:
Telephone number:

# Safety training and drills

## Safety training

Safety training should be given to employees so that they are aware of the following:
- what to do if they discover a fire
- how to raise an alarm of fire
- what to do if they hear the fire alarm
- where fire extinguishers are located and how to use them (if it safe to do so)
- escape routes from the building
- the whereabouts of the evacuation assembly point(s)
- how to call the Fire and Rescue Service
- arrangements for the evacuation of people with special needs
- the dangers associated with obstruction of fire exits and wedging open of fire resisting doors.

Safety training should be given to employees:
- at the time they are first employed,
- on their being exposed to new or increased risks, and,
- at periodic intervals as appropriate. (at least annually, depending upon the nature of the risk).

## Safety drills

Safety drills should be carried out at periodic intervals appropriate to the nature of the risk (a minimum of one safety drill each year is recommended).
During a safety drill:
- everyone should evacuate the premises except those that are required to keep the premises secure or where required to remain due to a process which cannot be shut down.
- you sufficiently check the procedures and arrangements for evacuating people with a disability
- encourage occupants to leave the building using an alternative escape route (where there is more than one escape route).
Where your fire alarm system is monitored, notify the alarm receiving centre before you start and once the drill has been completed.

# Record of safety training

Name	Date of appointment	Type of training/evacuation drill	Date	Name of trainer

Fire alarm system
The fire alarm test should be carried out in accordance with the manufacturer’s instructions and the current British Standard.

It is important that any testing of the fire alarm should not result in a false signal of fire.

Daily

Inspect the panel for normal operation of the system. Where provided, check that the connection to the monitoring centre is functioning correctly.

Weekly test by user

Carry out a test and examination to ensure that the system is capable of operating under alarm conditions.

Operate a manual call point at approximately the same time each week using a different call point for each successive test.

Where your fire alarm system is monitored contact the alarm receiving centre before you carry out the test and again, on completion to check the alarm signal was correctly received.

Periodic inspections and tests by a fire alarm engineer

These should be carried out by a competent person, e.g., a fire alarm engineer. Requirements for these inspections and tests will depend upon the type and design of the system.

Note: Where the weekly test proves onerous the Fire and Rescue Service may agree to it being carried out monthly. However, this only applies to certain modern fire alarm systems that are tested by a suitably competent person and where such a change of test frequency is supported by a risk assessment. No agreement will be given where automatic door release mechanisms operated by the fire alarm system are installed. Where such devices are installed the fire alarm should continue to be tested for operation weekly.
# Fire detectors
Carry out a regular visual inspection of each detector to check for damage, excessive accumulations of dirt, heavy deposits of paint and other conditions likely to interfere with correct operation.

Each detector should be checked and tested for correct operation and sensitivity in accordance with the manufacturer’s instructions and the current British Standard*.

## Measures to reduce unwanted alarms
False alarms will not only disrupt business operations but may also contribute to death or injury should Fire and Rescue Service resources be deployed answering false alarms when they should be attending incidents where life or property is in danger. To reduce the probability of false alarms on systems incorporating automatic fire detectors it is very important that a suitable system of testing and maintenance is in place. The cause of any false alarm should be properly investigated with measures being taken to avoid a repetition.

Do not call the fire service if the fire alarm activation is a confirmed false or unwanted alarm. If you have any doubts or there are signs of fire - call the fire service on 999 immediately.
All premises should have an emergency plan which includes a strategy for fire alarm activations and procedures, so the Fire Service is not called when there is a false alarm.
Alternatively, call the Fire Service to confirm a false alarm, as this will free our resources for confirmed fire and rescue emergencies.
Please contact your fire alarm maintenance and system monitoring providers for further advice.
You should discuss procedures with your alarm receiving centre to ensure that, where appropriate, they contact you to ascertain whether the alarm activation is caused by a fire, or a false alarm, before contacting the fire service. You should also consider a designated key-holder outside of your normal operating hours.
We strongly recommend that where your alarm monitoring company does pass a call to the fire service, designated key holders are also alerted, at the same time as the initial call, and are requested to attend the site within 20 minutes.
Typical causes
The following typical causes of false alarms can usually be avoided by improved awareness and by taking preventative measures.
General – including human factors
- Cooking fumes
- Steam
- Aerosol sprays
- Dust, small insects and thrips in detectors
- Smoking near detectors
- Controlled processes that produce smoke and fumes
- Water ingress
- Contractors including involved in hot works
- Mechanical damage/disruption
- Testing or maintenance of fire alarm systems without prior warning to the Alarm Receiving Centre (ARC)

Environmental
- Electrical storms
- Extreme fluctuation in temperature
- Pressure surges on water mains serving automatic sprinkler systems
- External smoke or fumes
- High air velocities

Technical
- Detector or alarm system equipment faults
- Testing or maintenance of fire alarm systems without prior warning to the Alarm Receiving Centre (ARC)
- Change of use of building, processes or occupants

A large proportion of the causes listed could easily be identified as false alarms by persons on or in the premises and hence not require a call to the Fire Service. This approach has proven successful where it has been implemented.
Therefore, dependent upon a suitable risk assessment of the premises, false alarm clarification prior to calling the Fire Service should be implemented. This approach should also be incorporated into the premises fire training programme.
The use of a predetermined time delay to allow fire marshals/responsible persons to identify and confirm obvious false alarms is to be strongly encouraged, subject to the premises risk assessment. It is no longer acceptable for premises to call the Fire Service, whether by 999 or by Alarm Receiving Centres (ARC) just because the alarm has activated without trying to implement management procedures (where possible) to identify false alarms.
If the premises are connected to an ARC, then a call back to confirm the cause of the activation prior to calling the Fire Service should be implemented.

# Automatic door release mechanisms activated by the fire alarm system

Weekly

All hold-open devices should be checked for correct operation, as part of the routine testing of the fire alarm system. A competent person should undertake any necessary maintenance.

The manufacturer's instructions should be closely followed, and an adequate record of testing and maintenance be kept. The batteries of devices with an integral power supply should be replaced in accordance with the manufacturer's instructions or every 12 months, whichever is most frequent.

Hold-open devices fitted to doors at either high or low level may, if used extensively, result in the doors becoming warped. Doors should not, therefore, be kept open more than necessary; preferably being kept closed at night or when the premises are unoccupied. Doors fitted with hold-open devices should be kept free from potential obstructions and be equipped with appropriate safety signs. Doors should be inspected frequently for signs of warping.

Note: All checks, tests and maintenance including faults and remedial action taken, should be recorded. The date on which each fault is rectified should also be recorded.
Further information on British Standards can be found by visiting the British Standards website: www.bsi-global.com

# Record of false / unwanted alarms
Date	Detail of False Alarm	Remedial action required	Date completed	Signature

# Fire alarm and automatic door release devices
## Record of tests
REMEMBER TO ISOLATE BEFORE TESTING
(If fire alarm is linked to an alarm receiving centre/monitoring station)
Date	Fire alarm call point/ detector location or number	Automatic door release(s) satisfactory		Remedial action required	Date completed	Name of tester (print)
		Yes	No

# Emergency lighting
Emergency lighting tests should be carried out in accordance with the manufacturer’s instructions and the current British Standard*.

Daily - Where there is a central power supply, carry out a visual inspection of indicators to ensure the system is in a ready condition.

Monthly – Simulate a failure of the normal lighting supply for sufficient time to allow all luminaires to be checked for correct operation.
Check each luminaire for any obvious signs of damage or deterioration, including the cleanliness and general condition of lenses and diffusers.
Annually - Simulate a failure of the normal lighting supply for the full duration of the battery and carry out a check of the charging arrangements to ensure proper functioning. This should normally be carried out when the building is empty or at a time of minimal risk.

Note: Regular servicing is essential. The occupier/owner of the premises shall appoint a competent person to supervise servicing of the system. This person shall be given sufficient authority to ensure the carrying out of any work necessary to maintain the system in correct operation.

All checks, tests and maintenance including faults and remedial action taken, should be recorded. The date on which each fault is rectified should also be recorded.

*Further information on British Standards can be found by visiting the British Standards website
www.bsi-global.com
# Emergency lighting
## Record of tests
Date	Type of test	Remedial action required	Date completed	Name of tester (print)

# Firefighting equipment
## Portable fire extinguishers
Portable fire extinguisher tests should be carried out in accordance with the manufacturer’s instructions and the current British Standard*.

Monthly - Check to ensure each extinguisher is in position, accessible, not discharged, damaged or lost pressure (if fitted with a pressure indicator) and that operating instructions are clean, legible and face outwards. Where circumstances require, e.g. where extinguishers are in exposed locations or particularly susceptible to theft or damage, the checks should be carried out more frequently.

Annually - Portable firefighting equipment should be inspected by a competent person in accordance with the manufacturers’ instructions and the British Standard*.

Note: All checks, tests and maintenance including faults and remedial action taken, should be recorded. The date on which each fault is rectified should also be recorded.

*Further information on British Standards can be found by visiting the British Standards website
www.bsi-global.com
# Fire extinguishers
## Record of tests
Date	Extinguisher location	Inspection or test	Remedial action required	Date completed	Name of tester / (print)

# Miscellaneous tests and checks
Means of escape, together with the measures provided for the protection of means of escape, should be inspected at periodic intervals.

The inspections should ensure all internal and external exit routes are unobstructed and that exit door furniture and fire-door self-closing devices operate efficiently.

Additionally, fire resisting doors and partitions should be in satisfactory repair and all safety signs and notices should be legible and properly displayed.

Note: All checks, tests and maintenance including faults and remedial action taken, should be recorded. The date on which each fault is rectified should also be recorded.

# Record of miscellaneous tests and checks
Date	Items tested/checked	Remedial action required	Date completed	Name of tester (print)